### Assessment Evidence Guide Template & Guidelines for Level 2 – 4 Qualifications

Section A: Instruction Sheet for Candidate(s)

| Qualification |  |
| --- | --- |
| Competency Standard(s) | - Apply Entrepreneurial Skill - Operate Hydraulics Machines - Calibrate Electrical Equipment - Diagnose Electrical Fault in Generator - Carryout Transmission of Electrical Power - Carryout Distribution of Electrical Power - Carryout Protection of Distribution and Transmission System - Install Turbine - Install Generator - Control HP plant shutdown for emergency standby electrical systems - Analyze faults in HP plant operation - Carry out preventive maintenance procedures as part of MHP operation - On Job Training |
| Purpose of Assessment | Formative / Summative / RPL |
| Candidate Details | Name________________________________________________________ Registration/Roll Number___________________ Date _________________ |

Section A1: Guidance for Candidate(s)

To be used on need-basis (prior to the assessments)

| General Guidance | To meet this assessment, the candidate(s) is/are required to complete the following Assessment Task 1: The generator is started, but the output voltage does not reach the rated voltage (e.g., 400V) and remains low (e.g., 250V) even at no-load. The voltage does not recover and remains low. |
| --- | --- |
| Time: | 00 Hrs. |
| Minimum Evidence Required | During a practical assessment, under observation by an assessor, the candidate(s) is/are required to: Assessment Task 1: The generator is started, but the output voltage does not reach the rated voltage (e.g., 400V) and remains low (e.g., 250V) even at no-load. The voltage does not recover and remains low. - Perform LOTO (Lockout tagout) on generator control panel. - Verify isolation by measuring terminal voltage - Inspect generator exterior: Check for burnt smell, loose cables, or visible damage. - Temporarily remove LOTO. - Start generator. - measure speed and terminal voltage - Check excitation system - Check AVR - Check Turbine speed - Restart generator. - Adopt safety protocols. - Complete fault report. |

Section A2: Self-Assessment Checklist

This section is optional for regular assessments and mandatory for RPL assessments

| Assessment Task 1 | Activity: The generator is started, but the output voltage does not reach the rated voltage (e.g., 400V) and remains low (e.g., 250V) even at no-load. The voltage does not recover and remains low. |
| --- | --- |

I (candidate) can……………….

| Performance Criteria | Yes | No |
| --- | --- | --- |
| - Perform LOTO (Lockout Tag out) on generator control panel. |  |  |
| - Verify isolation by measuring terminal voltage |  |  |
| - Inspect generator exterior: Checked for burnt smell, loose cables, or visible damage. |  |  |
| - Temporarily remove LOTO (Lockout Tag out) |  |  |
| - Start Generator. |  |  |
| - Measure speed and terminal voltage |  |  |
| - Check excitation system |  |  |
| - Check AVR |  |  |
| - Check Turbine speed |  |  |
| - Restart generator. |  |  |
| - Adopt safety protocols. |  |  |
| - Complete a fault report. |  |  |

Candidate’s Signature___________________ Assessor’s Signature_______________________

Date _______________________________

Section B: Assessor’s Judgement Guide

| Qualification |  |
| --- | --- |
| Competency Standard (s) | - Apply Entrepreneurial Skill - Operate Hydraulics Machines - Calibrate Electrical Equipment - Diagnose Electrical Fault in Generator - Carryout Transmission of Electrical Power - Carryout Distribution of Electrical Power - Carryout Protection of Distribution and Transmission System - Install Turbine - Install Generator - Control HP plant shutdown for emergency standby electrical systems - Analyze faults in HP plant operation - Carry out preventive maintenance procedures as part of MHP operation - On Job Training |
| Purpose of Assessment |  |
| Candidate Details | Name: ______________________________________________________________ Registration/Roll Number: ______________________ Signature: _______________ |
| Assessment Outcome | COMPETENT NOT YET COMPETENT Name of the Assessor________________________________________________ Assessor’s code: ____________________________________________________ Signature: ________________________________ |

| Assessment Summary (to be filled by the assessor) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Activity | Method |  |  |  |  | Result |  |
| Nature of Activity | Written | Oral | Observation | Portfolio | Role Play | Competent | Not Yet Competent |
| Practical Skill Demonstration |  |  | X |  | X |  |  |
| Knowledge Assessment | X | X |  |  |  |  |  |
| Other Requirement |  |  |  | X |  |  |  |

Section B1: Observation Checklist

| Assessment Task 1 |  | Activity: The generator is started, but the output voltage does not reach the rated voltage (e.g., 400V) and remains low (e.g., 250V) even at no-load. The voltage does not recover and remains low. |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| During the practical assessment, the candidate demonstrated the following: |  |  |  | Yes | No | Remarks |
|  | Perform LOTO (Lockout Tag out) on generator control panel. |  |  |  |  |  |
|  | Verify isolation by measuring terminal voltage |  |  |  |  |  |
|  | Inspect generator exterior: Checked for burnt smell, loose cables, or visible damage. |  |  |  |  |  |
|  | Temporarily remove LOTO (Lockout Tag out) |  |  |  |  |  |
|  | Start Generator. |  |  |  |  |  |
|  | Measure speed and terminal voltage |  |  |  |  |  |
|  | Check excitation system |  |  |  |  |  |
|  | Check AVR |  |  |  |  |  |
|  | Check Turbine speed |  |  |  |  |  |
|  | Restart generator. |  |  |  |  |  |
|  | Adopt safety protocols. |  |  |  |  |  |
|  | Complete a fault report. |  |  |  |  |  |
| Competent |  |  | Not Yet Competent |  |  |  |

Section B2: Knowledge Assessment

| Questions (Candidate confidently answered questions correctly and demonstrated understanding of the topics and their application) |  | Satisfactory | Not Satisfactory |
| --- | --- | --- | --- |
|  | What voltage reading must you confirm with a multimeter before touching generator terminals during LOTO? |  |  |
|  | If the AVR loses its AC power supply, what happens to the rotor’s DC field voltage? |  |  |
|  | What critical role does the AVR play in maintaining generator voltage? |  |  |
|  | Which generator part receives DC voltage: rotor or stator? |  |  |
|  | If generator speed drops below 1500 RPM, what happens to output voltage? |  |  |

Feedback to the Candidate

Candidate’s Signature__________________ Assessor’s Signature _________________ Date _________________