Instruction Sheet for the Candidate

| Qualification | National Vocational Certificate Level 4 in Mechatronics Technology |
| --- | --- |
| Competency Standard | Perform Tests On DC Generators |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name______________________________________________________ Registration/Roll Number_______________________________________ |
| Guidance for Candidate | To meet this standard, you are required to complete the following within time frame (for practical demonstration & assessment): - Plot the Open circuit characteristics of a Separately ExcitedD.C generator - Plot the Open circuit characteristics of a D.C shunt generator - Plot the load characteristics of D.C shunt generator. - Plot the load characteristics of D.C series generator. - Plot the load characteristics of D.C compound generator for under, flat and over compounding - Perform parallel operation of two DC shunt generators. - Determine copper, iron & friction losses of shunt generator by actual loading. |
| Time: 05 Hrs. | During a practical assessment, under observation by an assessor, you are required to |
| Minimum Evidence Required | - Plot the Open circuit characteristics of a Separately excitedD.C generator - Connect DC supply to field coil through rheostat and ampere meter. - Rotate armature at constant speed. - Connect voltmeter across armature terminal. - Decrease the resistance of rheostat in steps and measure and record the relevant output voltage of armature and field current. - Repeat the 2 to 4 till voltage of armature reach at its saturation point. - Plot the graph between field current and armature voltage from the recorded values. - Plot the Open circuit characteristics of a D.C shunt generator - Connect DC supply to field coil through rheostat and ampere meter. - Rotate armature at constant speed. - Connect voltmeter across armature terminal. - Decrease the resistance of rheostat in steps and measure and record the relevant output voltage of armature and field current. - Repeat the 8 to 10 till voltage of armature reach at its saturation point. - Plot the graph between field current and armature voltage from the recorded values. Subtract the value of back pitch from the added value. - Plot the load characteristics of D.C shunt generator. - Select DC shunt generator and connect variable load. - Connect ampere meter and voltmeter across the load. - Rotate armature at constant speed and note the readings of ampere meter and voltmeter. - Increase the load in steps till specific reduce in terminal voltage observed. - Plot the graph between load current and terminal voltage from the recorded values. - Plot the load characteristics of D.C series generator. - Select DC series generator and connect variable load. - Connect ampere meter and voltmeter across the load. - Rotate armature at constant speed and note the readings of ampere meter and voltmeter. - Increase the load in steps till specific reduce in terminal voltage observed. - Plot the graph between load current and terminal voltage from the recorded values. - Plot the load characteristics of D.C compound generator for under, flat and over compounding - Select DC compound generator and connect variable load. - Connect ampere meter and voltmeter across the load. - Rotate armature at constant speed and note the readings of ampere meter and voltmeter. - Adjust field diverter on zero ohm. - Increase the load in steps till specific reduce in terminal voltage observed. - Plot the graph between load current and terminal voltage from the recorded values. - Such off the load. - Adjust the field diverter at such position that the terminal voltages are equal to no load voltages. - Increase the load in steps till specific reduce in terminal voltage observed. - Plot the graph between load current and terminal voltage from the recorded values. - Switch off the load. - Adjust the field diverter at such position that the terminal voltages are greater than no load voltages. - Increase the load in steps till specific reduce in terminal voltage observed. - Plot the graph between load current and terminal voltage from the recorded values. - Perform parallel operation of two DC shunt generators. - Connect the circuit according to the circuit diagram. - Place all switches in off position. - Run generator 1 at rated speed. - Reduce field resistance of generator 1 - Connect generator with bus bar after attaining rated voltage. - Run generator 2 with prime mover. - Reduce the field resistance of generator 2 to attain its rated voltage. - Close the switches for parallel operation. - Calculate and record the reading of voltage and current on different loads. - Determine copper, iron & friction losses of shunt generator by actual loading. - Connect ammeter in series with both winding. - Connect voltmeter in parallel with both winding. - Apply 10-20 DC volt. - Record the readings of voltmeter and ammeter. - Calculate Ra and Rsh. - Run the generator at rated speed with prime mover. - Turn on the load switch and record the meter reading. - Calculate input power and output power. - Calculate total losses (Copper loss, Friction loss, Iron loss) |

Self-Assessment Checklist

| Candidate Name |  |
| --- | --- |
| Registration No. |  |
| Qualification | National Vocational Certificate Level 4 in Mechatronics Technology |
| Competency Standard | Perform Tests On DC Generators |
| Purpose of Assessment | Formative Assessment |
| Assessment Task | - Plot the Open circuit characteristics of a Separately ExcitedD.C generator - Plot the Open circuit characteristics of a D.C shunt generator - Plot the load characteristics of D.C shunt generator. - Plot the load characteristics of D.C series generator. - Plot the load characteristics of D.C compound generator for under, flat and over compounding - Perform parallel operation of two DC shunt generators. - Determine copper, iron & friction losses of shunt generator by actual loading. |

I can……………….

| Performance Criteria | Yes | No |
| --- | --- | --- |
| - Connect DC supply to field coil through rheostat and ampere meter. |  |  |
| - Rotate armature at constant speed. |  |  |
| - Connect voltmeter across armature terminal. |  |  |
| - Decrease the resistance of rheostat in steps and measure and record the relevant output voltage of armature and field current. |  |  |
| - Repeat the 2 to 4 till voltage of armature reach at its saturation point. |  |  |
| - Plot the graph between field current and armature voltage from the recorded values. |  |  |
| - Connect DC supply to field coil through rheostat and ampere meter. |  |  |
| - Rotate armature at constant speed. |  |  |
| - Connect voltmeter across armature terminal. |  |  |
| - Decrease the resistance of rheostat in steps and measure and record the relevant output voltage of armature and field current. |  |  |
| - Repeat the 8 to 10 till voltage of armature reach at its saturation point. |  |  |
| - Plot the graph between field current and armature voltage from the recorded values. Subtract the value of back pitch from the added value. |  |  |
| - Select DC shunt generator and connect variable load. |  |  |
| - Connect ampere meter and voltmeter across the load. |  |  |
| - Rotate armature at constant speed and note the readings of ampere meter and voltmeter. |  |  |
| - Increase the load in steps till specific reduce in terminal voltage observed. |  |  |
| - Plot the graph between load current and terminal voltage from the recorded values. |  |  |
| - Select DC series generator and connect variable load. |  |  |
| - Connect ampere meter and voltmeter across the load. |  |  |
| - Rotate armature at constant speed and note the readings of ampere meter and voltmeter. |  |  |
| - Increase the load in steps till specific reduce in terminal voltage observed. |  |  |
| - Plot the graph between load current and terminal voltage from the recorded values. |  |  |
| - Select DC compound generator and connect variable load. |  |  |
| - Connect ampere meter and voltmeter across the load. |  |  |
| - Rotate armature at constant speed and note the readings of ampere meter and voltmeter. |  |  |
| - Adjust field diverter on zero ohm. |  |  |
| - Increase the load in steps till specific reduce in terminal voltage observed. |  |  |
| - Plot the graph between load current and terminal voltage from the recorded values. |  |  |
| - Such off the load. |  |  |
| - Adjust the field diverter at such position that the terminal voltages are equal to no load voltages. |  |  |
| - Increase the load in steps till specific reduce in terminal voltage observed. |  |  |
| - Plot the graph between load current and terminal voltage from the recorded values. |  |  |
| - Switch off the load. |  |  |
| - Adjust the field diverter at such position that the terminal voltages are greater than no load voltages. |  |  |
| - Increase the load in steps till specific reduce in terminal voltage observed. |  |  |
| - Plot the graph between load current and terminal voltage from the recorded values. |  |  |
| - Connect the circuit according to the circuit diagram. |  |  |
| - Place all switches in off position. |  |  |
| - Run generator 1 at rated speed. |  |  |
| - Reduce field resistance of generator 1 |  |  |
| - Connect generator with bus bar after attaining rated voltage. |  |  |
| - Run generator 2 with prime mover. |  |  |
| - Reduce the field resistance of generator 2 to attain its rated voltage. |  |  |
| - Close the switches for parallel operation. |  |  |
| - Calculate and record the reading of voltage and current on different loads. |  |  |
| - Connect ammeter in series with both winding. |  |  |
| - Connect voltmeter in parallel with both winding. |  |  |
| - Apply 10-20 DC volts. |  |  |
| - Record the readings of voltmeter and ammeter. |  |  |
| - Calculate Ra and Rsh. |  |  |
| - Run the generator at rated speed with prime mover. |  |  |
| - Turn on the load switch and record the meter reading. |  |  |
| - Calculate input power and output power. |  |  |
| - Calculate total losses (Copper loss, Friction loss, Iron loss) |  |  |

Candidate’s Signature__________________ Assessor’s Signature____________________

Date: _______________________________

Assessors Judgment Guide

| Qualification | National Vocational Certificate Level 4 in Mechatronics Technology |
| --- | --- |
| Competency Standard | Perform Tests On DC Generators |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name: ______________________________________________________________ Registration/Roll Number: ______________________Signature: _______________ |
| Assessment Outcome | COMPETENT NOT YETCOMPETENT Name of the Assessor________________________________________________ Assessor’s code:____________________________________________________ Signature: ________________________________ |

| Assessment Summary (to be filled by the assessor) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Activity | Method |  |  |  |  | Result |  |
| Nature of Activity | Written | Oral | Observation | Portfolio | Role Play | Competent | Not Yet Competent |
| Practical Skill Demonstration |  |  |  |  |  |  |  |
| Knowledge Assessment |  |  |  |  |  |  |  |
| Other Requirement |  |  |  |  |  |  |  |

Observation Checklist

| Assessment Task |  | - Identify Plot the Open circuit characteristics of a Separately ExcitedD.C generator - IdentifyPlot the Open circuit characteristics of a D.C shunt generator - IdentifyPlot the load characteristics of D.C shunt generator. - IdentifyPlot the load characteristics of D.C series generator. - IdentifyPlot the load characteristics of D.C compound generator for under, flat and over compounding - IdentifyPerform parallel operation of two DC shunt generators. - IdentifyDetermine copper, iron & friction losses of shunt generator by actual loading. |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| During the practical assessment, candidate demonstrated the following: |  |  |  | Yes | No | Remarks |
|  | Identified Connected DC supply to field coil through rheostat and ampere meter. |  |  |  |  |  |
|  | IdentifiedRotated armature at constant speed. |  |  |  |  |  |
|  | IdentifiedConnected voltmeter across armature terminal. |  |  |  |  |  |
|  | IdentifiedDecreased the resistance of rheostat in steps and measure and recorded the relevant output voltage of armature and field current. |  |  |  |  |  |
|  | IdentifiedRepeated the 2 to 4 till voltage of armature reach at its saturation point. |  |  |  |  |  |
|  | IdentifiedPlotted the graph between field current and armature voltage from the recorded values. |  |  |  |  |  |
|  | IdentifiedConnected DC supply to field coil through rheostat and ampere meter. |  |  |  |  |  |
|  | IdentifiedRotated armature at constant speed. |  |  |  |  |  |
|  | IdentifiedConnected voltmeter across armature terminal. |  |  |  |  |  |
|  | IdentifiedDecreased the resistance of rheostat in steps to measure and record the relevant output voltage of armature and field current. |  |  |  |  |  |
|  | IdentifiedRepeated the 8 to 10 till voltage of armature reach at its saturation point. |  |  |  |  |  |
|  | IdentifiedPlotted the graph between field current and armature voltage from the recorded values. Subtract the value of back pitch from the added value. |  |  |  |  |  |
|  | IdentifiedSelected DC shunt generator and connect variable load. |  |  |  |  |  |
|  | IdentifiedConnected ampere meter and voltmeter across the load. |  |  |  |  |  |
|  | IdentifiedRotated armature at constant speed and note the readings of ampere meter and voltmeter. |  |  |  |  |  |
|  | IdentifiedIncreased the load in steps till specific reduce in terminal voltage observed. |  |  |  |  |  |
|  | IdentifiedPlotted the graph between load current and terminal voltage from the recorded values. |  |  |  |  |  |
|  | IdentifiedSelected DC series generator and connect variable load. |  |  |  |  |  |
|  | IdentifiedConnected ampere meter and voltmeter across the load. |  |  |  |  |  |
|  | IdentifiedRotated armature at constant speed and note the readings of ampere meter and voltmeter. |  |  |  |  |  |
|  | IdentifiedIncreased the load in steps till specific reduce in terminal voltage observed. |  |  |  |  |  |
|  | IdentifiedPlotted the graph between load current and terminal voltage from the recorded values. |  |  |  |  |  |
|  | IdentifiedSelected DC compound generator and connected variable load. |  |  |  |  |  |
|  | IdentifiedConnected ampere meter and voltmeter across the load. |  |  |  |  |  |
|  | IdentifiedRotated armature at constant speed and note the readings of ampere meter and voltmeter. |  |  |  |  |  |
|  | IdentifiedAdjusted field diverter on zero ohm. |  |  |  |  |  |
|  | IdentifiedIncreased the load in steps till specific reduce in terminal voltage observed. |  |  |  |  |  |
|  | IdentifiedPlotted the graph between load current and terminal voltage from the recorded values. |  |  |  |  |  |
|  | IdentifiedSwitched off the load. |  |  |  |  |  |
|  | Identified Adjusted the field diverter at such position that the terminal voltages are equal to no load voltages. |  |  |  |  |  |
|  | IdentifiedIncreased the load in steps till specific reduce in terminal voltage observed. |  |  |  |  |  |
|  | IdentifiedPlotted the graph between load current and terminal voltage from the recorded values. |  |  |  |  |  |
|  | IdentifiedSwitched off the load. |  |  |  |  |  |
|  | IdentifiedAdjusted the field diverter at such position that the terminal voltages are greater than no load voltages. |  |  |  |  |  |
|  | IdentifiedIncreased the load in steps till specific reduce in terminal voltage observed. |  |  |  |  |  |
|  | IdentifiedPlotted the graph between load current and terminal voltage from the recorded values. |  |  |  |  |  |
|  | IdentifiedConnected the circuit according to the circuit diagram. |  |  |  |  |  |
|  | IdentifiedPlaced all switches in off position. |  |  |  |  |  |
|  | IdentifiedRun generator 1 at rated speed. |  |  |  |  |  |
|  | IdentifiedReduced field resistance of generator 1 |  |  |  |  |  |
|  | IdentifiedConnected generator with bus bar after attaining rated voltage. |  |  |  |  |  |
|  | IdentifiedRun generator 2 with prime mover. |  |  |  |  |  |
|  | IdentifiedReduce the field resistance of generator 2 to attain its rated voltage. |  |  |  |  |  |
|  | IdentifiedClose the switches for parallel operation. |  |  |  |  |  |
|  | IdentifiedCalculate and recorded the reading of voltage and current on different loads. |  |  |  |  |  |
|  | IdentifiedConnect ammeter in series with both winding. |  |  |  |  |  |
|  | IdentifiedConnectvoltmeter in parallel with both winding. |  |  |  |  |  |
|  | IdentifiedApply 10-20 DC volt. |  |  |  |  |  |
|  | IdentifiedRecord the readings of voltmeter and ammeter. |  |  |  |  |  |
|  | IdentifiedCalculate Ra and Rsh. |  |  |  |  |  |
|  | IdentifiedRun the generator at rated speed with prime mover. |  |  |  |  |  |
|  | IdentifiedTurn on the load switch and recorded the meter reading. |  |  |  |  |  |
|  | IdentifiedCalculate input power and output power. |  |  |  |  |  |
|  | IdentifiedCalculate total losses (Copper loss, Friction loss, Iron loss) |  |  |  |  |  |
| Competent |  |  | Not Yet Competent |  |  |  |

Knowledge Assessment

| Qualification | National Vocational Certificate Level 4 in Mechatronics Technology |
| --- | --- |
| Competency Standard | Perform Tests On DC Generators |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name:______________________________________________________________ Registration/Roll Number: _________________ Candidate Signature:___________ |
| Assessment Outcome | COMPETENT NOT YETCOMPETENT Name of the Assessor:________________________________________________ Assessor’s code:____________________________________________________ Signature of the Assessor:_______________________ |

Candidate’s response is not required to be identical, but similar concepts and/or keywords must be used. Oral questioning may be used to clarify candidate understanding of topic and its application.

| Questions (Candidate confidently answered questions correctly and demonstrated understanding of the topics and their application) |  | Satisfactory | Not Satisfactory |  |
| --- | --- | --- | --- | --- |
|  | What is different between shunt and separately excited generator? |  |  |  |
|  | Explain the effect of rheostat resistance on terminal voltage. |  |  |  |
|  | What is armature reaction? |  |  |  |
|  | Explain the reason of voltage reduce due to increase in load. |  |  |  |
|  | How to compensate armature reaction? |  |  |  |
|  | What is copper loss? |  |  |  |
|  | What is iron loss? |  |  |  |

Feedback to the Candidate

Candidate’s Signature__________________ Assessor’s Signature _________________