National Vocational Certificate Electrical Technology (Industrial Electrician)

Level-3

Curriculum

National Vocational and Technical Training Commission (NAVTTC)

Government of Pakistan

FOREWORD

National Vocational and Technical Training Commission (NAVTTC) extends its gratitude and appreciation to representatives of business, industry, academia, government agencies, provincial TEVTAs, sector skill councils and trade associations who spared time and extended their expertise for the development of National Vocational Qualification for Electrical Technology (Industrial Electrician)-Level-3. This work was made possible with the technical support of the experts.

It may not be prudent to mention here that all the industry experts from P@SHA and other private industries, Academic experts from UET Peshawar, University of Baluchistan, Institute of Management & Sciences Peshawar and Shaheed Benazir Bhutto Women University Peshawar, and TVET experts of TEVTAs, BTEs, PVTC, work diligently for making this qualification worthy and error-free for which all credit goes to them. However, NAVTTC accepts responsibility for all the errors and omissions still prevailing in the Qualification document.

It is also noteworthy that development of Skill Standards is a dynamic and ongoing process, and the developed competency standards needs periodic review and updating owing to the constant technological advancements, development in scientific knowledge, and growing experience of implementation at the grass root level as well as the demand of industry. The NAVTTC, Government of Pakistan will ensure to keep the qualifications abreast with the changing demands of both national and international job markets.

Executive Director (NAVTTC)

Table of Contents

1.	Introduction	4

1.1.	Date of Development	4

1.2.	Date of Review and Validation	4

1.3.	Entry Requirement	4

1.4.	Minimum qualification for teachers	4

1.5.	Medium of instruction	4

1.6.	Duration of Course	4

2.	Scheme of Studies	5

3.	Overview of the Curriculum for Electrical Technology (Industrial Electrician)- Leve l-3 	6

4.	Details of Modules	8

0713E&E1-Verify Basic Laws of Electromagnetic Induction 	8

0713E&E2-Operate/Perform Associated Tests on Transformer	15

0713E&E3-Identify Vector Group of Three Phase Transformer	21

00713E&E4-Install Three Phase Complex Electrical Wiring 	27

0713E&E5-Perform Testing of Electrical Three Phase Wiring	38

00713E&E6-Repair/ Maintenance of Electrical Installations for three Phase	44

0713E&E7-Maintain Professionalism in the Workplace and Advance Green Practices	48

5.	List of Personal Protective Equipment (For A Class Of 25 Students)	55

6.	List of Tools and Equipment	56

7.	Members of Qualification Development Committee	64

# Introduction

Green skills incorporation in TVET aims to build capacity of skilled workforce, which is aware of environmental hazards and accordingly adopts more sustainable and environment friendly practices at the workplace. The workforce that possesses competencies and relevant knowledge & understanding oriented to green occupations is more employable and become an asset for businesses, enterprises and communities in developing green economies that results in improved human well-being and reducing environmental risks.

The United Nation’s Sustainable Development Goals (SDGs), UNESCO ESD initiatives UNEVOC, ILO, CPSC and ADB guidelines, studies and training manuals provide comprehensive green skill strategies to develop competencies / skills that can be imparted under vocational education and training. They are focused to prepare the workforce to adopt sustainable practices and address environmental degradation by appropriately managing human and material resources.

The vocational professions are increasingly getting attention in Pakistan, not only among the youth seeking to enter in the job market but also among adults who wish to polish their skills to develop a career out of it. The scope and demand of Domestic or General Electrician is very high in Pakistan due to fast growing population and construction projects in Pakistan. There are more job opportunities for electricians in Pakistan than any other vocational field. Pakistan is still facing energy crises, therefore needs more power houses, dams, renewable energy sources, solar installations etc. which will result in more demand of electrical technicians. Pakistan can boost economic growth and job creation by overcoming inefficiencies in its power sector. Power sector reforms that address these distortions can make better use of existing facilities. These need to focus on eliminating waste, promoting the shift towards cleaner energy and attracting private investments.

The Government of Pakistan through National Vocational & Technical Training Commission (NAVTTC) in collaboration with German Development Company & BMZ has revised the national vocational qualifications for NVQF level 1 to Level 3 in Electrical Technology with greening concepts, which not only allows trainees to equip with growing Industrial trends but will be beneficial in rapidly capturing the job market across the globe.

This document identifies competencies related to electrician trade identified by the relevant industry during workshops held at Lahore Chamber of Commerce & Industry, Lahore. These skills either can be infused as a separate competency standard / competency unit in relevant qualifications or can be integrated as a separate module in the qualifications already developed or being developed under growth economic sectors. Critical evidence statements have also been added to assist assessors in preparation and conduct of assessment. The purpose of this document is to bring change in abilities, values and attitudes needed by human to support the sustainable and effective utilization of resources in the workplace. It focuses on the skills that will help preserve and conserve the environment. If qualifications implemented by training providers, will directly benefit the poor by increasing access, improving reliability, and reducing cost and pollution.

| ## Date of Development | 25 – 30 August 2025 |
| --- | --- |
| ## Date of Review and Validation | 23rd May, 2025 |
| ## Entry Requirement | Must have Secondary School Certificate or Equivalent with National Vocational Certificate Level -2 in Electrical Technology |
| ## Minimum qualification for teachers | - B.Sc. Engineering and 2 years of relevant work experience; or - B-Tech/ BS Technology and 3 years of relevant work experience; or - Diploma Associate Engineer (DAE) and 5 years relevant work experience; or - Certificate as Electrician (G-II) with 8 years relevant work experience |
| ## Medium of instruction | English/ Urdu |
| ## Duration of Course | Total. 600 hours. Theory. 120 hours Practical. 480 hours |

# Overall objectives of training program

0713E&E0301-Verify Basic Laws of Electromagnetic Induction

0713E&E0302-Operate/Perform Associated Tests on Transformer

0713E&E0303-Identify Vector Group of Three Phase Transformer

0713E&E0304-Install Three Phase Complex Electrical Wiring

0713E&E0305-Perform Testing of Electrical Three Phase Wiring

0713E&E0306-Repair/ Maintenance of Electrical Installations for three Phase

0713E&E0307-Maintain Professionalism in the Workplace and Advance Green Practices

# Scheme of Studies

| Module Code | Name of Competency | NVQF Level | Category | Contact Hour |  |  | Credit |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Th. | Pr. | Total |  |
| 0713E&E0301 | Verify Basic Laws of Electromagnetic Induction | 3 | Technical | 10 | 40 | 50 | 5 |
| 0713E&E0302 | Operate/Perform Associated Tests on Transformer | 3 | Technical | 30 | 120 | 150 | 15 |
| 0713E&E0303 | Identify Vector Group of Three Phase Transformer | 3 | Technical | 10 | 50 | 60 | 6 |
| 0713E&E0304 | Install Three Phase Complex Electrical Wiring | 3 | Technical | 24 | 116 | 140 | 14 |
| 0713E&E0305 | Perform Testing of Electrical Three Phase Wiring | 3 | Technical | 10 | 40 | 50 | 5 |
| 0713E&E0306 | Repair/ Maintenance of Electrical Installations for three Phase | 3 | Technical | 30 | 90 | 120 | 12 |
| 0713E&E0307 | Maintain Professionalism in the Workplace and Advance Green Practices | 3 | Generic | 6 | 24 | 30 | 3 |
| Total |  |  |  | 120 | 480 | 600 | 60 |

# Overview of the Curriculum Level-3 for Electrical Technology (Industrial Electrician)

| Module Title | Learning Units | Theory hours | Workplace hours | Timeframe of modules |
| --- | --- | --- | --- | --- |
| 0713E&E0301-Verify Basic Laws of Electromagnetic Induction | - Verify Faraday’s law by moving permanent magnet inside the coil. - Verify Faraday’s law by moving coil near the magnet field. - Verify Faraday’s law using relative motion of coil and magnet. - Perform Faraday’s Law using simple loop generator. - Verify Torque induce in a current carrying loop - Verify Mutual induction | 10 | 40 | 50 |
| 0713E&E0302-Operate/Perform Associated Tests on Transformer | - Operate Single Phase Transformer - Perform Tests on Single Phase Transformer - Operate Auto Transformer - Perform Tests on Auto Transformer - Operate Three Phase Transformer | 30 | 120 | 150 |
| 0713E&E0303-Identify Vector Group of Three Phase Transformer | - Connect 3-phase transformers as per given vector group Yyo and Yy6 - Connect 3-phase transformers as per given vector group Ddo and Dd6 - Connect 3-phase transformers as per given vector group Yd11 and Yd1 | 10 | 50 | 60 |
| 0713E&E0304-Install Three Phase Complex Electrical Wiring | - Make and Install 3phase motor connection Reverse/ forward by Magnetic contactor. - Make and Install 3-phase motor connection Reverse/ forward by Magnetic contactor with indicator. - Make and Install 3 phase motor connection Star/Delta (Manual) by Magnetic contactor - Make and Install 3 phase motor connection Star/Delta (Manual) by Magnetic contactor with indicator. - Make and Install 3 phase motor connection Star/Delta (Auto) by Magnetic contactor - Make and Install 3 phase motor connection Star/Delta (Auto) by Magnetic contactor with indicator - Make and Install 3 phase motor connection 2 speed by Magnetic contactor. - Make and Install 3 phase motor connection 2 speed by Magnetic contactor with indicator - Perform Electrical Work for Industrial Area. | 24 | 116 | 140 |
| 0713E&E0305-Perform Testing of Electrical Three Phase Wiring | - Perform Open Circuit Test - Perform Short Circuit Test - Perform Continuity/Loop Test - Perform Visual Test - Perform Polarity Test - Perform Earth Resistance Test - Perform BLAVIER & Earth Loop Test | 10 | 40 | 50 |
| 0713E&E0306-Repair/ Maintenance of Electrical Installations for three Phase | - Analyze Fault in Electrical Installations - Repair Fault in Electrical Installations | 30 | 90 | 120 |
| 0713E&E0307-Maintain Professionalism in the Workplace and Advance Green Practices | - Establish personal work goals - Set and meet own work priorities - Develop and maintain professional competence - Implement Advance Green Practices | 6 | 24 | 30 |
| Total |  | 120 | 480 | 600 |

# Details of Modules

## 0713E&E0301	Verify Basic Laws of Electromagnetic induction Objective:

This module covers on the skills and knowledge required to verify various aspects of Faraday's law, which is a fundamental principle of electromagnetism. The module also focuses on maintaining green TVET concept by adopting 6 R’s of Green Skills I.e. Recycle, Reduce, Reuse, Renew, Repair, Rethink concepts.

Duration: 50 Hours	Theory: 10 Hours	Practice: 40 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials (Tools & & Equipment) Required | Duration |
| --- | --- | --- | --- | --- | --- |
| - Verify Faraday’s law by moving permanent magnet inside the coil. | - Construct a coil. - Connect Galvanometer with coil. - Move permanent magnet inside the coil fast and slow. - Record the effect of movement of magnet on reading of Galvanometer. - Hold the magnet inside the coil and do not move. - Record the effect on reading of Galvanometer again. | - Construction technique of making coil and connection of coil with galvanometer - Procedure of taking reading from galvanometer after the change the movement of magnet inside the coil. - Faraday’s First Law of Electromagnetic Induction. - Faraday’s Second Law of Electromagnetic Induction. Practical Activity Verify Faraday’s Law of Electromagnetic Induction, - Coil is connected to a galvanometer and a permanent magnet is moved in and out of the coil at different speeds. - Galvanometer shows deflection during motion and no deflection when the magnet is stationary, - Confirming that emf is induced only due to relative motion between the magnet and the coil. | Total :10Hrs. Theory: 02 Hrs. Practical: 08 Hrs. | - Coil - Galvanometer. - Magnet. Consumable Materials - Connecting leads. | Class Room and workshop |
| - Verify Faraday’s law by moving coil near the magnet field. | - Construct a coil. - Connect Galvanometer with coil. - Fix permanent magnet and move the coil fast and slow on it. - Record the effect of movement of coil on reading of Galvanometer. - Hold the coil near the magnetic field and do not move. - Record the effect on reading of Galvanometer. | - Coil is moved near the fixed magnet an induced current is generated in the coil. - Compare the galvanometer readings when the coil is moved. - Procedure of taking reading from galvanometer after the movement of coil near the magnet. - Coil is held stationary near the magnet, no deflection occurs. - Role of relative motion between in the coil and magnetic field to produce emf. - Induced emf depends on the rate of change of magnetic flux. Practical Activity Verify Faraday’s Law of Electromagnetic Induction, - Coil connected to a galvanometer is moved at different speeds near a fixed magnet, - Produce deflections, while no deflection occurs when held stationary. - Confirms that emf is induced only by relative motion between the coil and the magnetic field. | Total :10-Hrs. Theory:02 Hrs. Practical:08 Hrs. | - Coil - Galvanometer. - Connecting leads. - Magnet. Consumable Materials - Connecting leads. | Class Room and workshop |
| - Verify Faraday’s law using relative motion of coil and magnet. | - Construct a coil. - Connect Galvanometer with coil. - Make relative motion of coil and magnet. - Record the effect of movement on reading of Galvanometer. | - Faraday’s Law. using relative motion of coil and magnet. - Role of relative motion in producing emf. - Construction technique of coil and connection of coil with galvanometer - Procedure of taking reading from galvanometer after the relative motion of coil and magnet. Practical Activity Verify Faraday’s Law of Electromagnetic Induction, - Coil is constructed and connected to a galvanometer. By creating relative motion between the coil and a magnet, - Deflections are observed on the galvanometer, - Confirm that emf is induced only due to their relative motion. | Total: 08-Hrs. Theory:01 Hrs. Practical:07 Hrs. | - Coil - Galvanometer. - Magnet. Consumable Materials - Connecting leads. | Class Room and workshop |
| - Verify Faraday’s Law using simple loop generator. | - Identify single loop generator and its parts. - Select field winding. - Connect Galvanometer with single loop coil. - Rotate the single loop coil of generator in the field - Measure the voltage induces in loop generator. - Record the effect of movement on reading of Galvanometer. | - Main parts of a single-loop generator and explain their function. - Field winding and its role in a loop generator. - Rotating the single-loop coil in a magnetic field induces voltage. - Rotation of single loop coil in magnetic field. - Effect of movement on the reading of Galvanometer. Practical Activity Verify Faraday’s Law of Electromagnetic Induction - A single loop generator is identified and connected to a galvanometer. - Loop coil is rotated in the magnetic field, and the induced voltage is measured. - Deflections on the galvanometer during rotation - Confirm that emf is generated due to the relative motion of the coil within the magnetic field. | Total :10Hrs. Theory:02 Hrs. Practical:08 Hrs. | - Loop - Galvanometer. - Voltmeter - coil - DC source Consumable Materials - Connecting leads. | Class Room and workshop |
| - Verify Torque induce in a current carrying loop | - Construct a coil. - Apply DC voltage to this coil. - Place a current carrying loop in this coil. - Check the direction of force to verify the torque produce. | - Torque in the context of a current-carrying conductor in a magnetic field. - Main parts required to construct a coil for the experiment. - Application of DC voltage to the coil produces a magnetic field. - Knowledge of Fleming’s Left-Hand Rule. - Current-carrying loop in the coil Practical Activity Verify that torque is induced in a current-carrying loop, - Coil is constructed and supplied with DC voltage. - Current-carrying loop is placed inside the coil, the direction of force acting on the loop is observed, - Confirm the production of torque due to the interaction between current and magnetic field. | Total :08-Hrs. Theory:01 Hrs. Practical:07 Hrs. | - Coil - Voltmeter - DC source - Loop Consumable Materials - Connection Leads | Class Room and workshop |
| - Verify Mutual induction | - Construct 2 coils on two different legs of single core. - Apply AC voltage to the any one coil. - Check the volts induce in another coil by voltmeter. | - Mutual induction and describe its significance in electrical circuits. - Electrical machine work on the principle of mutual induction - Construction of two coils on two different legs of single core transformer. - Procedure of checking mutual induction. Practical Activity Verify Mutual Induction, - Two coils are wound on separate legs of a single core. An AC voltage is applied to one coil, - Induced voltage is measured in the other coil using a voltmeter - Confirm the principle of mutual induction. | Total: 04-Hrs. Theory:02 Hrs. Practical: 02 Hrs. | - Coils - Voltmeter - core - AC source Consumable Materials - Connection Leads | Class Room and workshop |

## 0713E&E0302 Operate/Perform Associated Tests on Transformer

Objective:

This module covers the skills and knowledge required to Operate/Perform Associated Tests on Transformer. Also covers the knowledge and skills required to perform polarity test of single-phase transformer, Perform Open circuit test of transformer, Perform Short Circuit Test of Transformer, calculate efficiency of transformer by direct method and calculate efficiency of transformer by Back-to-Back test. The module also focuses on maintaining green TVET concept by adopting 6 R’s of Green Skills

Duration: 150 Hours	 Theory: 30 Hours	Practice:120Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials (Tools & Equipment) Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Operate Single Phase Transformer | - Identify types of transformers. - Make transformer winding - Measure transformation ratio of single-phase transformer. - Determine voltage regulation of single-phase transformer with different load. - Perform parallel operation of single-phase transformer | - Types of transformers and their applications. - Transformation ratio in a single-phase transformer. - Purpose of transformer windings in voltage transformation. - Voltage regulation is affected by varying loads. - Propose a simple testing method to check the accuracy of a single-phase transformer’s voltage regulation. - Parallel operation of single-phase transformer Practical Activity Perform the following Tests on Single Phase Transformer - Identify types of transformers. (Core types/ shell types) - Make transformer winding connection primary and secondary side using of all measuring instruments - Measure transformation ratio of single-phase transformer. - Conduct voltage regulation of single-phase transformer with different load. - Conduct parallel operation of single-phase transformer. | Total :30 Hrs. Theory: 06 Hrs. Practical: 24 Hrs. | - Electrician Tool Kit - Multimeter - Clamp meter - Single phase transformer - Advance electrical trainer completes with all accessories and practical’s manual (TLM) Consumable Materials - Connection Leads | Class Room and workshop |
| - Perform Tests on Single Phase Transformer | - Perform polarity test of single-phase transformer. - Perform Open circuit test of transformer. - Perform Short circuit test of transformer. - Calculate efficiency of transformer by direct method. - Calculate efficiency of transformer by Back-to-Back test. | - Polarity test is performed on a single-phase transformer to determine the relative polarity of the primary and secondary windings. - Purpose of an open-circuit test in transformers - Procedure of a short-circuit test and what parameters it helps to determine. - Difference between direct efficiency testing and back-to-back testing of a transformer. - Calculate the efficiency of a transformer using the direct loading method. Practical Activity Perform the following Tests on Single Phase Transformer - Polarity test of single-phase transformer. - Open circuit test of transformer. - Short circuit test of transformer. - Measure the input &Output power of transformer using electrical instruments then calculate efficiency of transformer - Back-to-Back (Regenerative) test is conducted using two identical single-phase transformers connected in a back-to-back configuration. | Total: 30 Hrs. Theory: 06 Hrs. Practical: 24 Hrs. | - Electrician Tool Kit - Multimeter - Clamp meter - Single Phase Transformer - Advance electrical trainer completes with all accessories and practical’s manual (TLM) Consumable Materials - Connection Leads | Class Room and workshop |
| - Operate Auto Transformer | - Identify the connection of auto transformer. - Calculate Voltage ratio of auto transformer. - Calculate Current ratio of auto transformer. | - Term an auto transformer and its main applications. - Winding connection of an auto transformer differs from that of a two-winding transformer. - Calculate the voltage ratio of an auto transformer given the tapping points. - Calculate Current ratio of auto transformer. - Advantages & disadvantages of using an auto transformer compared to a two-winding transformer. Practical Activity Perform the following Tests using the Auto Transformer - Identify the connection of auto transformer (Supply side and load side). - Measure Voltage ratio of auto transformer. - Measure Current ratio of auto transformer. - Compare the reading of measuring method & Calculate method | Total: 30 Hrs. Theory: 06 Hrs. Practical: 24 Hrs. | - Electrician Tool Kit - Multimeter - Clamp meter - Auto transformer - Advance electrical trainer completes with all accessories and practical’s manual (TLM) Consumable Materials - Connection Leads | Class Room and workshop |
| - Perform Tests on Auto Transformer | - Perform open circuit test of auto transformer. - Perform short circuit test of auto transformer. - Calculate efficiency of auto transformer | - Purpose of an open-circuit test on an auto transformer. - Parameter can be determined from a short-circuit test on an auto transformer. - Difference between open-circuit and short-circuit tests in terms of the losses they measure. - Calculate the efficiency of an auto transformer using test data of (Open Circuit (OC) Test, Short Circuit (SC) Test Load data (usually kVA, load power factor, and load level). - Advantage of efficiency testing in auto transformers compared to direct loading methods. Practical Activity Perform the following Tests using the Auto Transformer - open circuit test of auto transformer. - short circuit test of auto transformer. - Measure the input & Output power of auto transformer using electrical instruments then calculate efficiency of transformer | Total 30 Hrs. Theory. 06 Hrs. Practical: 24 Hrs. | - Electrician Tool Kit - Multimeter - Clamp meter - Auto transformer - Advance electrical trainer completes with all accessories and practical’s manual (TLM) Consumable Materials - Connection Leads | Class Room and workshop |
| - Operate Three Phase Transformer | - Make three phase transformer winding. - Perform star to star connection of three phase transformer. - Perform star to delta connection of three phase transformer. - Perform delta to delta connection of three phase transformer. - Perform delta to star connection of three phase transformer. - Connect two single phase transformers in open delta. - Perform parallel operation of 3 phase transformers | - Different types of three-phase transformer connections (star–star, star–delta, delta–delta, delta–star). - Procedure for making a three-phase transformer winding. - Characteristic of star–delta connections in terms of voltage, current, and load sharing. - Connect two single-phase transformers to form an open-delta configuration. - Characteristic of delta–delta connections in terms of voltage, current, and load sharing. - Parallel operation of 3- phase transformers Practical Activity Perform the following Tests/activity using of Three Phase Transformer - Make the connection of transformer in Star-to-Star configuration - Make the connection of transformer in Star to Delta configuration - Make the connection of transformer in Delta-to-Delta configuration - Make the connection of transformer in Delta to Star configuration - Connect two single phase transformers in open delta. - Make the connection for parallel operation of 3-phase transformer | Total: 30 Hrs. Theory: 06 Hrs. Practical: 24 Hrs. | - Electrician Tool Kit - Multimeter - Clamp meter - Single phase transformer - Three phase transformers - Advance electrical trainer completes with all accessories and practical’s manual (TLM) Consumable Materials - Connection Leads | Class Room and workshop |

## 0713E&E0303 Identify Vector Group of Three Phase Transformer Objective:

This module covers skills and knowledge required to connect three-phase transformers in different vector group configurations. The module also focuses on maintaining green TVET concept by adopting 6 R’s of Green

Duration: 60 Hours		Theory: 10 Hours		Practice: 50 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials (Tools& Equipment) Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| - Connect 3-phase transformers as per given vector group Yyo and Yy6 | - Connect three identical single-phase transformers in star-to-star connection. - Connect phase angle meter between primary and secondary. - Apply rated voltage to the primary side of transformer. - Measure the phase angle between primary and secondary with the help of phase angle meter (00 and 1800). | - Characteristic of Star-to-star connection in three phase transformers - Procedure for connecting three identical single-phase transformers in a star-to-star configuration - Connection of phase angle meter between primary and secondary of the transformers. - The Phase angle of vector group Yy0. - Phase angle of vector group Yy6 Practical Activity Perform the following Tests/activity using of Transformer - Construct a three-phase transformer bank by connecting three identical single-phase transformers in a star-to-star (Y-Y) configuration. as per given vector group Yyo and Yy6 - Connect a phase angle meter between the primary and secondary windings, - Apply the rated voltage to the primary side, - Measure the phase displacement to analyze the relationship between primary and secondary voltages. - Verifying the displacement values of 0° and 180° in accordance with the respective vector groups. | Total 19 Hrs. Theory: 03 Hrs. Practical: 16 Hrs. | - Single phase transformers. - Three phase transforms - Phase angle meter. - AC source. - Multimeter - Insulation tester - Wattmeter - Advance electrical trainer complete with all accessories and practical’s manual (TLM) Consumable Materials •Connection Leads | Class Room and workshop |
| - Connect 3-phase transformers as per given vector group Ddo and Dd6 | - Connect three identical single-phase transformers in delta-to-delta connection. - Connect phase angle meter between primary and secondary. - Apply rated voltage to the primary side of transformer. - Measure the phase angle between primary and secondary with the help of phase angle meter (00 and 1800). | - Characteristic of delta-to-delta connection in 3- phase transformer - Vector group of a three-phase transformer and explain its significance. - Difference Characteristic between Yy0 and Yy6 vector groups. - Procedure for connecting three identical single-phase transformers in a delta-to-delta configuration. - Advantages and disadvantages of connecting a phase angle meter between the primary and secondary windings of a three-phase transformer. - Phase displacement between primary and secondary windings in Yy0 and Yy6 connections. - Importance of proper vector group selection for parallel operation of transformers. Practical Activity Perform the following Tests/activity using of Transformer - Construct a three-phase transformer bank by connecting three identical single-phase transformers in a delta-to-delta (Dd) configuration as per the given vector groups Dd0 and Dd6. - Connect phase angle meter will be between the primary and secondary windings. - Apply the rated voltage to the primary side, you will use the phase angle meter to - Measure and analyze the phase displacement between the primary and secondary voltages, - Verifying the displacement values of 0° and 180° in accordance with the respective vector groups. | Total 19 Hrs. Theory: 03 Hrs. Practical: 16 Hrs. | - Single phase transformers. - Three phase transforms - Phase angle meter. - AC source. - Multimeter - Insulation tester - Wattmeter - Advance electrical trainer complete with all accessories and practical’s manual (TLM) Consumable Materials • Connection Leads | Class Room and workshop |
| - Connect 3-phase transformers as per given vector group Yd11 and Yd1 | - Connect three identical single-phase transformers in star to delta connection. - Connect phase angle meter between primary and secondary. - Apply rated voltage to the primary side of transformer. - Measure the phase angle between primary and secondary with the help of phase angle meter (300 lag or 300 lead). | - The Yd vector group in a three-phase transformer. - Key difference between Yd11 and Yd1 connections. - Procedure for connecting three identical single-phase transformers in a star-to-delta configuration. - Connection of phase angle meter between the windings of a three-phase transformer vector group configuration Yd11 and Yd1. - The phase displacement between primary and secondary is 30° lag for Yd11 and 30° lead for Yd1. - Importance of correct vector group identification when connecting transformers in parallel. Practical Activity Perform the following Tests/activity using of Transformer - Construct a three-phase transformer bank by connecting three identical single-phase transformers in a star-to-star (Y-Y) configuration. as per given vector group Yd11 and Yd1 - Connect a phase angle meter between the primary and secondary windings, - Apply the rated voltage to the primary side, - Measure the phase displacement to analyze the relationship between primary and secondary voltages. - Verifying the displacement values of 0° and 180° in accordance with the respective vector groups. | Total: 22 Hrs. Theory: 04 Hrs. Practical: 18 Hrs. | - Single phase transformers. - Three phase transforms - Phase angle meter. - AC source. - Multimeter - Insulation tester - Wattmeter - Advance electrical trainer complete with all accessories and practical’s manual (TLM) Consumable Materials • Connection Leads | Class Room and workshop |

## 0713E&E0304	Install Three Phase Complex Electrical Wiring

Objective:

This module covers the skills and knowledge the trainees will be able to make and install three Phase complex electrical wiring.

Duration: 140 Hours			Theory: 24 Hours				Practice: 116 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials (Tools& Equipment) Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Make and Install 3 phase motor connection Reverse/ forward by Magnetic contactor. | - Draw power diagram of circuit. - Draw control diagram of circuit. - Draw installation diagram of circuit. - Mark on exercise board according to installation/layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply | - Function and connection of Magnetic Contactor used for 3- phase motor Reversing circuit. - Thermal overload relay, function and connection with 3-phase induction motor. - Function and connection of Push button - Create the installation, power, and control circuit diagrams for a 3-phase motor connection in Reverse/ forward configuration, incorporating a circuit breaker, Push button Overload relays and magnetic contactors - Application of 3 phase motor connection Reverse/ forward by Magnetic contactor. Practical Activity - Install the Power and control circuit 3-phase motor connection Reverse/ forward by Magnetic contactor | Total:16. Hrs Theory:3. Hrs. Practical:13 Hrs. | - Electrician Tool kit, - 3 phase motor, - Multi meter. - Magnetic Contactors, - Tachometer Consumable Materials - Connection Leads - PVC wires - Circuit breakers - Lamp - Insulation Tape - Connector bar - PVC cable | Class Room and workshop |
| Make and Install 3 phase motor connection Reverse/ forward by Magnetic contactor with indicator. | - Draw power diagram of circuit. - Draw control diagram of circuit. - Draw installation diagram of circuit. - Mark on exercise board according to installation/layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply | - Function and connection of Magnetic Contactor used for 3- phase motor Reversing circuit. - Thermal overload relay function and connection with 3-phase induction motor. - Function and connection of Push button - Create the installation, power, and control circuit diagrams for a 3-phase motor connection in Reverse/ forward with indicators configuration, incorporating a circuit breaker, Push button, Overload relays and magnetic contactors - Application of 3 phase motor connection Reverse/ forward by Magnetic contactor. Practical Activity - Install the Power and control circuit 3-phase motor connection Reverse/ forward by Magnetic contactor with indicator. | Total:16. Hrs Theory:3. Hrs. Practical:13. Hrs. | - Electrician Tool kit, - 3 -phase Induction motor. - Multi meter. - Magnetic Contactors - Tachometer Consumable Materials - Connection Leads - PVC wires - Circuit breakers - Lamp - Insulation Tape - Connector bar - PVC cable - Push Button | Class Room and workshop |
| Make and Install 3 phase motor connection Star/Delta (Manual) by Magnetic contactor. | - Draw power diagram of circuit. - Draw control diagram of circuit. - Draw installation diagram of circuit. - Mark on exercise board according to installation/layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply. | - Function and application of Star -Delta connection in 3 phase motor - Operation of 3 phase motor connection Star/Delta (Manual) by Magnetic contactor. - Function and connection of Magnetic Contactor used for 3- phase motor star /delta circuit. - Importance of thermal overload relay, its function and connection with 3-phase induction motor. - Function and connection of Push button - Create the installation, power, and control circuit diagrams for a 3-phase motor connection in star/Delta configuration, incorporating a circuit breaker, Push button, Overload relays and magnetic contactors Practical Activity - Install the Power and control circuit of 3-phase motor connection Star/Delta (Manual) by Magnetic contactor. | Total:16. Hrs Theory:3. Hrs. Practical:13. Hrs. | - Electrician Tool kit, - 3 phase induction motor, - Magnetic contactor - Multi meter. - Push Button - Tachometer Consumable Materials - Connection Leads - PVC wires - Circuit breakers - Lamp - Insulation Tape - Connector bar - PVC cable - Push Button | Class Room and workshop |
| Make and Install 3 phase motor connection Star/Delta (Manual) by Magnetic contactor with indicator. | - Draw power diagram of circuit. - Draw control diagram of circuit. - Draw installation diagram of circuit. - Mark on exercise board according to installation/layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply | - Function and application of Star -Delta connection in 3 phase motor - Operation of 3 phase motor connection Star/Delta (Manual) by Magnetic contactor. - Function and connection of Magnetic Contactor used for 3- phase motor star /delta circuit. - Thermal overload relay, its function and connection with 3-phase induction motor. - Importance the function and connection of Push button - Create the installation, power, and control circuit diagrams for a 3-phase motor connection in star/Delta configuration, incorporating a circuit breaker, Push button Overload relays and magnetic contactors Practical activity: - Install the Power and control circuit of 3-phase motor connection Star/Delta (Manual) by Magnetic contactor. With indicator | Total:16. Hrs Theory:3. Hrs. Practical:13. Hrs. | - Electrician Tool kit, - 3 phase induction motor, Star/Delta - Multi meter. Contactors, Cables. - Indicators - Tachometer - AC Motor trainer complete with all accessories and practical’s manual (TLM) Consumable Materials - Connection Leads - PVC wires - Circuit breakers - Lamp - Insulation Tape - Connector bar - PVC cable - Push Button | Class Room and workshop |
| Make and Install 3 phase motor connection Star/Delta (Auto) by Magnetic contactor. | - Draw power diagram of circuit. - Draw control diagram of circuit. - Draw installation diagram of circuit. - Mark on exercise board according to installation/layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply | - Function and application of timer in Star -Delta (Auto) connection by Magnetic contactor. - Function and application of Star -Delta (Auto) connection in 3 phase motor - Operation of 3 phase motor connection Star/Delta (Auto) by Magnetic contactor. - Function and application of Magnetic Contactor used for 3- phase motor star /delta circuit. - Importance of thermal overload relay, its function and connection with 3-phase induction motor. - Create the installation, power, and control circuit diagrams for a 3-phase motor connection in star/Delta (Auto) configuration, incorporating a circuit breaker, Push button, Overload relays and magnetic contactors Practical activity: - Install the Power and control circuit of 3-phase motor connection Star/Delta (Auto) by Magnetic contactor. | Total:16. Hrs Theory:3. Hrs. Practical:3. Hrs. | - Electrician Tool kit, - 3 phase motor Star/Delta - Multi meter. - Magnetic Contactors - Timer - Tachometer - AC Motor trainer complete with all accessories and practical’s manual (TLM) Consumable Materials - Connection Leads - PVC wires - Circuit breakers - Lamp - Insulation Tape - Connector bar - PVC cable | Class Room and workshop |
| Make and Install 3 phase motor connection Star/Delta (Auto) by Magnetic contactor with indicator | - Draw power diagram of circuit. - Draw control diagram of circuit. - Draw installation diagram of circuit. - Mark on exercise board according to installation/layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply | - Function and application of timer in Star -Delta (Auto) connection in 3 phase motor - Function and application of Star -Delta (Auto) connection in 3 phase motor - Operation of 3 phase motor connection Star/Delta (Auto) by Magnetic contactor. - Function and connection of Magnetic Contactor used for 3- phase motor star /delta circuit. - Create the installation, power, and control circuit diagrams for a 3-phase motor connection in star/Delta (Auto) with indicators configuration, incorporating a circuit breaker, Push button Overload relays and magnetic contactors Practical activity: - Install the Power and control circuit of 3-phase motor connection Star/Delta (Auto) by Magnetic contactor. With indicator with indicators | Total:16. Hrs Theory:3. Hrs. Practical:13. Hrs. | - Electrician Tool kit, - 3 phase induction motor, Star/Delta - Multi meter. - Magnetic Contactors, - Timer - Tachometer - AC Motor trainer complete with all accessories and practical’s manual (TLM) Consumable Materials - Connection Leads - PVC wires - Circuit breakers - Lamp - Insulation Tape - Connector bar - PVC cable - Push Button | Class Room and workshop |
| Make and Install 3 phase motor connection 2 speed by Magnetic contactor. | - Draw power diagram of circuit. - Draw control diagram of circuit. - Draw installation diagram of circuit. - Mark on exercise board according to installation/layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply | - Function and application of 2-Speed Induction Motor. - Function and connection of Magnetic Contactor used for 3- phase motor connection 2 speed by Magnetic contactor. - Create the installation, power, and control circuit diagrams for a 3-phase motor connection in 2- speed configuration, incorporating a circuit breaker, Push button Overload relays and magnetic contactors Practical activity: - Install the Power and control circuit of 3- phase motor connection 2 speed by Magnetic contactor. | Total:15. Hrs Theory: Hrs. Practical:13. Hrs. . | - Electrician Tool kit, - 3 phase Induction motor 2- speed, - Multi meter. - Magnetic Contactors, - Tachometer - AC Motor trainer complete with all accessories and practical’s manual (TLM) Consumable Materials - Connection Leads - PVC wires - Circuit breakers - Lamp - Insulation Tape - Connector bar - PVC cable - Push Button | Class Room and workshop |
| Make and Install 3 phase motor connection 2 speed by Magnetic contactor with indicators | - Draw power diagram of circuit. - Draw control diagram of circuit. - Draw installation diagram of circuit. - Mark on exercise board according to installation/layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply. | - Function and application of 2-Speed Induction Motor. - Function and connection of Magnetic Contactor used for 3 phase motor connection 2 speed by Magnetic contactor. - Thermal overload relay, its function and connection with 3-phase induction motor. - Create the installation, power, and control circuit diagrams for a 3-phase motor connection in 2- speed with indicators configuration, incorporating a circuit breaker, Push button Overload relays and magnetic contactors Practical activity: - Install the Power and control circuit of 3- phase motor connection 2- speed by Magnetic contactor with indicator | Total:15. Hrs Theory:2. Hrs. Practical:13. Hrs. | - Electrician Tool kit, - 3 phase Induction motor 2- speed, - Multi meter. - Magnetic Contactors, - Indicator - Tachometer - AC Motor trainer complete with all accessories and practical’s manual (TLM) Consumable Materials - Connection Leads - PVC wires - Circuit breakers - Lamp - Insulation Tape - Connector bar - PVC cable - Push Button | Class Room and workshop |
| - Perform Electrical Work for Industrial Area. | - Install Main Distribution BOX.as per the given task - Install wire for grounding in given task. - Install circuit Breakers and switch gears in main box/ distribution Box, as per load for safety measures - Install change over switch for emergency light system in main box distribution Box, as per standard color scheme - Laying conduits or Trunks in the as per drawing - Install electrical wiring, as per drawing and standard. - Install main box OR distribution box. | - Types, application and function of Main Distribution Box (DB) in electrical system - Basic components installed in a distribution box. - Advantages and disadvantages of a change-over switch in Electrical Work for Industrial area. - Standard color codes of electrical wiring. - Function of grounding wire in a distribution system. - Important of standard electric cable color scheme in electrical wiring system. - Role of circuit breakers and switchgear in electrical safety. - Differentiate between a main box and a sub-distribution box Practical activity: - Install a Main Distribution Box in accordance with the given Load connection diagram in Workshop/Lab as per drawing given. All tasks will be carried out by adhering to safety standards and specifications, ensuring that the installation of the main distribution box is complete, functional, and meets quality standards. The details of installation in DB (Main Distribution Box) are consist of following items/ electrical accessories - Install Circuit Breakers, natural strip, Voltmeters, Amperemeters, indicators with make the connection of all electrical accessories - Install a change-over switch will be to connect the emergency lighting system, ensuring reliability during power failures. | Total:4. Hrs Theory:2. Hrs. Practical:12. Hrs. | - Voltmeters, - Amperemeters - change-over switch - Multi meter. - Indicators Consumable Materials - Connection Leads - PVC wires - Circuit breakers - Lamp - Insulation Tape - Connector bar - PVC cable - DB (Main Distribution Box) - Circuit Breakers, | Class Room and workshop |

## 0713E&E0305	Perform Testing of Electrical Three Phase Wiring

Objective:

This module covers the skills and knowledge required to perform Testing of Electrical Three Phase Wiring

Duration: 50 Hours        	Theory: 10 Hours 	Practice: 40 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials (Tools & Equipment) Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| LU1. Perform Open Circuit Test | - Perform open circuit with line tester in given task - Perform open circuit with Test boy equipment in the given task. | - Differences between open circuit and short circuit tests in three-phase wiring systems. - Equipment used for open circuit and short circuit testing (line tester, test boy, etc.). - Basic principle of an open circuit and its effect on current flow. - Characteristics of open circuit test with a line tester and test boy equipment in three-phase wiring system. Practical activity - Perform an open circuit test on a three-phase wiring system using a line tester and test boy to verify circuit integrity regarding open circuit test - Test will confirm the absence of continuity in de-energized circuits, locate breaks in phase, neutral, or earth conductors, and ensure correct identification of open versus short circuit conditions. - All procedures will be carried out safely with the supply isolated. | Total: 9-Hrs. Theory: 2-Hrs. Practical: 07-Hrs. | - Digital Multimeter - Insulation tester - Megger Meter Consumable Materials - Connection Leads - PVC wires | - Classroom / workshop |
| LU2. Perform Short Circuit Test |  | - Cool check Open DB or given task and look in DB for any short circuit OR burned cable. - Remove shortage with a suitable method OR replace the burned cable | - Purpose of a cool check in an open distribution board (DB). in three-phase wiring - Types of instruments used for testing of short circuit test in three-phase wiring Practical Activity - Perform a short circuit test on a three-phase wiring system by first carrying out a cool check of the open distribution board (DB) or the assigned task. - During inspection, the trainee will observe and identify any short circuit condition or burned cable inside the DB. - Fault is detected, analyze the problem and select a suitable method to remove the short circuit fault. - Replace the burned cable with a standard cable according to safety procedures and electrical specifications. | Total: 8 Hrs. Theory: 1 Hrs. Practical: 07Hrs. | - Digital Multimeter - Insulation tester - Megger Meter Consumable Materials - Connection Leads - PVC wires | - Classroom / workshop |
| LU3. Perform Continuity/Loop Test |  | - Connect all metal-clad switches, metal parts, and conduits with earth. - Open the main switch. - Turn on all the switches. - Connect earth continuity tester with conduit and independent earth. | - Purpose of continuity test in verifying the proper flow of current in electrical conductors in three phase wiring - Definition & types of main switch - Procedure to connect earth continuity tester with conduit and independent earth Practical Activity - Perform a continuity test to verify the integrity of the electrical installation's earthing system. After ensuring safety by opening the main switch, all metal-clad switches, metallic parts, and conduits will be confirmed as bonded to earth. - Using an earth continuity tester, a measurement will be taken between a conduit and the independent earth terminal to check for a continuous low-resistance path. - The results will be observed and interpreted to confirm full compliance with established electrical safety standards. | Total: 07- Hrs. Theory: 1-Hrs. Practical: 06Hrs | - Distribution Box (DB) - Tool Kit - Cable Stripper - Thimble Plier Consumable Materials - Connection Leads - PVC wires | - Classroom / workshop |
| LU4. Perform Visual Test |  | - Check the joints of the wire. - Check if there is any spark. - Check overheating of wires. - Check all the appliances are looking in good condition. - Check all indications of meters. - Check Voltages on all phases. - Check the DB and Breakers. - Check the main supply is coming properly. | - Visual test in electrical installation and its purpose. - Key components to be inspected during a visual test (wires, joints, appliances, meters, DB, breakers). - Common signs of faults such as sparks, overheating, or damaged insulation. - Importance of visual testing in monitoring sparks and overheating to prevent electrical hazards. - Purpose of verifying voltages on all phases during a visual test. Practical Activity - Conduct a comprehensive visual inspection of the 3-phase electrical installation to identify defects or hazards. - Check wire joints for integrity, signs of sparking or overheating, and ensure all appliances and components are in good condition. - Inspect the distribution board and circuit breakers for damage, verify correct main supply connection, and confirm all phase voltages are within acceptable limits via meter readings. | Total: 6-Hrs Theory: 1-Hrs. Practical: 05-Hrs. | - Digital Multimeter - Insulation tester - Earth resistance tester Consumable Materials - Connection Leads - PVC wires | - Classroom / workshop |
| LU5. Perform Polarity Test |  | - Switch off the main switch. - Disconnect all loads. - Switch on all circuit control switches. - Connect the ohmmeter between the main line and all the terminals of sockets and load points one by one. - Ensure the meter-reading value must be less than 1 ohm. | - Polarity test and its importance in electrical installation. - Purpose of switching off the main switch and disconnecting loads before testing. - Advantages and Disadvantages of Correct Methods for Polarity Testing in Electrical Wiring Using electrical testing instrument5s - Significance of Obtaining a Reading of Less Than 1 Ohm and Its Relation to Confirming Proper Wiring, Continuity, and Grounding in a Circuit. Practical Activity - Perform a three-phase polarity test by isolating the supply, disconnecting loads, and closing all control switches. - Use an ohmmeter to verify continuity between each supply phase (L1, L2, L3) and corresponding points at outlets and loads. - Verify the reading of instruments below 1 ohm confirms correct phasing and termination, with no cross-phasing or neutral faults. | Total: 7 Hrs Theory: 2 Hrs. Practical: 05- Hrs. | - Digital Multimeter - Insulation tester - Megger Consumable Materials - Connection Leads - PVC wires | - Classroom / workshop |
| LU6. Perform Earth Resistance Test |  | - Place 3 electrodes on earth at a distance of 10m apart between every electrode. - Connect terminal E of the earth resistance tester to the first electrode. - Connect terminal P of the earth resistance tester to the second electrode. - Connect terminal C of the earth resistance tester with third electrode. - Measure the resistances after applying specific voltage. - Repeat P1 to P5 by interacting earthling regions. - Ensure 3 readings must be equal. | - Earth resistance and its importance in electrical safety. - Equipment used for earth resistance testing (e.g., earth tester / megger). - Importance to perform an earth resistance test in electrical installations. - Working principle of an earth resistance tester. - Factors affecting earth resistance (soil condition, moisture, electrode depth, etc.). Practical Activity - Conduct an earth resistance test by placing three electrodes 10 meters apart. Connect the tester (E to electrode 1, P to electrode 2, C to electrode 3), measure resistance, and repeat across different locations to obtain three consistent readings. simultaneously - verify three-phase wiring polarity by isolating the supply, closing all circuit switches, and using an ohmmeter to confirm continuity (less than 1 ohm) between each phase (L1, L2, L3) and corresponding load/outlet points, ensuring correct phasing and no neutral faults. | Total: 6-Hrs Theory: 1 Hrs. Practical:5-Hrs. | - Digital Multimeter - Insulation tester - Megger - Earth Resistance Test Meter Consumable Materials - Connection Leads - PVC wires | - Classroom / workshop |
| LU7. Perform BLAVIER & Earth Loop Test |  | - Perform given task with Erath leakage tester - Connect the tester to the system as per the BLAVIER method | - Blavier Test and Earth Loop Test in electrical installations. - Equipment’s required (earth leakage tester) for performing the test. - Purpose of performing Blavier and Earth Loop Tests in ensuring system safety. - Working principle of an earth leakage tester. - Importance of low-resistance loop paths for fault current protection. Practical Activity - perform the Blavier and Earth Loop Test using an earth leakage tester to verify the effectiveness of the earthing system and electrical safety. - Tester will be connected as per instructions, readings observed, and results interpreted to confirm adequate protection against leakage currents and a low-resistance loop path for fault currents. | Total: 07-Hrs Theory: 2Hrs. Practical: 5-Hrs. | - Digital Multimeter - Insulation tester - Megger - Erath leakage tester Consumable Materials - Connection Leads - PVC wires | - Classroom / workshop |

## 0713E&E0306	Repair/ Maintain Electrical Installations for Three Phase

## Objective:

This module covers the skills and knowledge for a trainee to Analyze Faults in Electrical Installations, troubleshoot of electrical equipment, and Carry out Preventive Maintenance, repair, and maintenance work in accordance with the manufacturer’s instructions and organizational requirements.

Duration: 120 Hours        	Theory: 30 Hours 	Practice: 90 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials (Tools & Equipment) Required | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Analyze Fault in Electrical Installations | - Inspect visually the electrical wiring, fixtures, equipment, soldering, connection, appliances and machinery for discovering the faults and defects - Check the installation for consistency with the electrical drawing - Draw the layout of equipment's before disassembling of electrical components - Check the faulty components with scope or meter - Re assembled the components as per drawing and the installation - Check the fault indication at the relay for HT installation - Test electrical equipment as specified in the manufacturer’s manual and record the results | - Understanding of layout diagrams, technical sketches, graphic symbols, wiring diagrams, and manufacturer’s specifications etc. - Types of electrical tools used for testing and preventive maintenance purposes - Methods of tracing the fault in electrical installation Practical activity: Analyze and repair Electrical wiring faults of the Work shop /Lab - Identify common faults in electrical wiring, fixtures, equipment, soldering, connections, appliances, and machinery - Demonstrate the correct method of drawing the layout of equipment before disassembling electrical components. - Inspect visually the electrical wiring, fixtures, equipment, soldering, connections, appliances, and machinery to discover faults and defects. - Test electrical equipment the electrical wiring, fixtures, equipment, soldering, connections, appliances, and machinery to discover faults and defects - Rectification and final Testing of the electrical wiring, fixtures, equipment, soldering, connections, appliances, and machinery to discover faults and defects | Total:60. Hrs. Theory:15Hrs Practical:45 Hrs. | - Multi meter, - Megger, - Electrical tool kit, - Mechanical tool kit, - Battery Cleaning Kit, - Earth Tester, - Filler gauge, Generator, Consumable Materials - Connection Leads - PVC wires | Class Room and workshop |
| - Repair Fault in Electrical Installations | - Prepare a list of items/material(s) required for repair /replacement as per specifications - Draw circuit diagram of electrical equipment's be disassembling - Make necessary adjustments in the control and protective switchgear - Replace defective control & protective switch gear, cables and accessories with standard items - Replace defective earth electrode & faulty/damaged earthling conductors - Test installed electrical equipment for safe and optimum performance according to standards & regulations - Record the results of the test performed on a standard format | - Types of electrical control and protective switchgear and accessories used in electrical circuits - Types and principles of operation of circuit breakers used in electrical installations and their applications - Types of electrical wires and cables and their ratings - Types of electrical accessories and their applicant electrical installations - Purpose of earthing systems used in domestic& industrial Electrical installations - Importance of testing electrical installations. - Importance of corrective & preventive maintenance in electrical installations. Practical Activity Perform repairing task for given scenario/Task of Electrical Installations for Three Phase - Identify common faults in electrical wiring, fixtures, equipment, soldering, connections, appliances, and machinery - Demonstrate the correct method of drawing the layout of equipment before disassembling electrical components. - Inspect visually the electrical wiring, fixtures, equipment, soldering, connections, appliances, and machinery to discover faults and defects. - Test electrical equipment the electrical wiring, fixtures, equipment, soldering, connections, appliances, and machinery to discover faults and defects - Rectification and final Testing of the electrical wiring, fixtures, equipment, soldering, connections, appliances, and machinery to discover faults and defects | Total:60 Hrs Theory:15Hrs Practical:45 Hrs. . | - Multi meter, - Megger, - Electrical tool kit, - Mechanical tool kit, - Battery Cleaning Kit, - Earth Tester, - Filler gauge, Generator, Consumable Materials - Connection Leads - PVC wires | Class Room and workshop |

## 0713E&E0307	 Maintain professionalism in the workplace and advance Green Practices

Objective:

This module covers the skills and knowledge required to create systems and processes to organize information and prioritize tasks. It applies to individuals working in managerial positions who have excellent organizational skills. Also adopted green practices.

Duration: 30 Hours        	Theory: 6 Hours 	Practice: 24 Hours

| Learning Unit | Learning Outcomes | Learning Elements | Duration | Materials (Tools & Equipment) | Learning Place |
| --- | --- | --- | --- | --- | --- |
| Establish personal work goals | - Serve as a positive role model in the workplace through personal work planning - Ensure personal work goals, plans, and activities reflect the organization s plans, and own responsibilities and accountabilities - Measure and maintain personal performance in varying work conditions, work contexts, and when contingencies occur | - Personal work goals and explain their importance in the workplace. - Significance of Personal Work Planning in Role Modeling Workplace Excellence - Key elements that personal work goals and plans should reflect according to organizational objectives. - Role of personal responsibilities and accountabilities influence work planning. - Methods for measuring and maintaining personal performance under varying work conditions and contingencies. Practical Activity: - Develop a work plan that aligns with your organization’s mission and objectives. Practice measuring your performance and adapting the plan to manage real-life workplace challenges, such as shifting deadlines, resource shortages, or unexpected events. - Prepare a report documenting tasks completed, observations, challenges, and solutions.” | Total-:7 Hrs Theory:1 Hrs Practical:6 Hrs | - Computer with Internet Consumable Materials - Stationary - Sign boards | - Classroom / workshop |
| Set and meet own work priorities | - Take initiative to prioritize and facilitate competing demands to achieve personal, team and organizational goals and objectives - Use technology efficiently and effectively to manage work priorities and commitments - Maintain appropriate work-life balance, and ensure stress is effectively managed and health is attended to | - Proactive Prioritization and Initiative for Organizational Goal Achievement - Key Aspects of aligning Work Priorities and Planning to Meet Performance Targets in organization - Strategies to maintain an appropriate work-life balance. - Importance of managing stress and attending to personal health while meeting work priorities. Practical Activity: - Make a group of Trainees (Max-5 Nos) in the electrical field will autonomously prioritize and execute tasks using digital planning tools in a simulated high-pressure environment, managing stress, maintaining work-life balance, and ensuring health. - Performance is evaluated on task efficiency, effective technology use, and sustainable self-management. | Total:7 Hrs Theory:1 Hrs Practical:6 Hrs | - Computer with Internet Consumable Materials - Stationary - Sign boards | - Classroom / workshop |
| Develop and maintain professional competence | - Assess personal knowledge and skills against competency standards to determine development needs, priorities and plans - Seek feedback from employees, clients and colleagues and use this feedback to identify and develop ways to improve competence - Identify, evaluate, select and use development opportunities suitable to personal learning style/s to develop competence - Participate in networks to enhance personal knowledge, skills and work relationships - Identify and develop new skills to achieve and maintain a competitive edge | - Professional competence and explain its importance in the workplace. - Method of personal knowledge and skills can be assessed against competency standards. - Seek and use feedback from employees, clients, and colleagues to improve competence. - Types of development opportunities suitable for various learning styles. - Key Benefits of Professional Networking to enhance personal knowledge, skills, and work relationships - Importance of identifying and developing new skills to maintain a competitive edge. Practical Activity: - Make a group of Trainees (Max-5 Nos) will assess their electrical knowledge and skills against competency standards, seek feedback from colleagues and clients, and use it to improve performance. - Make the report of this activity | Total: 8 Hrs Theory:2 Hrs Practical:6 Hrs | - Computer with Internet Consumable Materials - Stationary - Sign boards | - Classroom / workshop |
| - Implement Advance Green Practices | - Implement sustainable and environmentally friendly practices in precision electrical field - Implement strategies to reduce environmental impact and promote biodiversity - Record and report environmental data to the supervisor. | - Advantages of advanced green practices in the precision electrical field. - Importance of implementing sustainable and environmentally friendly practices at work. - Strategies that can reduce environmental impact and promote biodiversity. - Process of recording and reporting environmental data to a supervisor. - Impact of Green Practices on Organizational Sustainability and Environmental Responsibility Practical Activity: - Trainees will implement sustainable strategies in precision electrical tasks, including waste reduction, material recycling, and energy efficiency measures. - Record and report environmental data (e.g., waste metrics, energy savings) to Teacher - Performance will be assessed on effective adoption of eco-friendly practices, data accuracy, and demonstrated commitment to reducing environmental impact. - Make the report of this activity | Total-:8 Hrs Theory:2 Hrs Practical:6 Hrs | - Computer with Internet Consumable Materials - Stationary - Sign boards | - Classroom / workshop |

# List of Personal Protective Equipment (For A Class Of 25 Students)

| Name of Trade |  |  |  |
| --- | --- | --- | --- |
| Duration of Course |  | 6 Months |  |
| Sr. # | Description |  | Quantity |
|  | Safety Helmet |  | 25 Nos |
|  | Safety vest |  | 25 Nos |
|  | Safety Shoes |  | 25 Nos |
|  | Safety Gloves |  | 25 Nos |
|  | Safety googles |  | 25 Nos |
|  | Ear Plugs |  | 25 Nos |
|  | Safety Mask |  | 25 Nos |

# List of Tools and Equipment

| SN | Tools | Quantity |
| --- | --- | --- |
| 1 | Computer with Internet | 01Nos |
| 2 | Stationary | 01Nos |
| 3 | Sign boards | 01Nos |
| 4 | Multimedia | 01Nos |
| 5 | Printer | 01Nos |

| List of Tools / Equipment For 25 Trainee |  |  |
| --- | --- | --- |
| Sr. No. | Name of Tools / Equipment | Quantity |
|  | Screw Driver flat and plus type set off 4”, 6”, 8” | 25 Nos each |
|  | Neon phase tester light duty pocket size | 25 Nos |
|  | Insulated pliers with side cutter | 25 Nos |
|  | Insulated long nose pliers with side cutter | 25 Nos |
|  | Insulated wire cutter | 25 Nos |
|  | High insulation rubber hand gloves | 5 Nos |
|  | Insulated Electrical Knife | 25 Nos |
|  | Chisels 6”, 12” | 10 Nos each |
|  | Hammers 200 grm. | 25 Nos |
|  | Hand Hack saws 12”, 6” with blade | 25 Nos each |
|  | Electric soldering iron 45, 100 and150 watt 220V | 10 Nos each |
|  | Wire Strippers | 25 No,s |
|  | Philips screw driver No 1, 2, 3. | 25 Nos each |
|  | Measuring tap 3m | 25 Nos |
|  | Steel foot rule. | 25 Nos |
|  | Files (Flat) 250 x 1, 200 x 2 | 05 Nos each |
|  | Files (Triangular) 150 x 2 | 05 Nos |
|  | Files (Half round) 200 x 2 | 05 Nos |
|  | Files (Round) 200 x 1 | 05 Nos |
|  | Files (Raps cut) 150 | 05 Nos |
|  | Bench Vice 5” | 05 Nos |
|  | Tri square 150 x 100 mm | 05 Nos |
|  | Vernier caliper 150 mm (Digital) | 05 Nos |
|  | Center punch | 05 Nos |
|  | Hammer 500 grm | 05 Nos |
|  | Scriber | 05 Nos |
|  | Rubber hammer | 05 Nos |
|  | Vice clamps | 05 Nos |
|  | Insulation Remover 150 mm | 25 Nos |
|  | Bearing puller | 2 Nos |
|  | Farmer chisels 8”. | 05 Nos |
|  | Wooden saw 300 mm | 05 Nos |
|  | Test boy tester with all accessories | 25 Nos |
|  | Volt meter Analogue (Panel type 4” x 4”) 0-300V-AC 50 HZ | 25 Nos |
|  | Ammeter Analogue (Panel type 4” x 4”) 0-300V-AC 50 HZ | 25 Nos |
|  | Multi-meter A.C / D.C (Digital) (voltage, Current, OHM, frequency, Uf, Continuity and Diode test) | 25 Nos |
|  | Basic electrical trainer completes with DC Power supply with suitable voltage for law. # Basic Electrical Trainer – With All Accessories and Practical’s Manual (TLM) verify fundamental laws of electromagnetism and transformer principles: - Verify Basic Laws of Electromagnetic Induction by: (Moving a permanent magnet inside the coil, Moving the coil near the magnetic field, Using relative motion of coil and magnet) - Perform Faraday’s Law using a Simple Loop Generator - Verify Torque Induced in a Current-Carrying Loop - Verify Mutual Induction using coupled coils ### Trainer Components Coils & Magnetic Setup: Air-core and iron-core coils /Permanent magnets and electromagnet arrangements - Simple Loop Generator Assembly - Coupled Coils for Mutual Induction - DC/AC Power Supply (Low Voltage, Safe for Lab Use) - Digital Meters: Voltmeter, Ammeter, Galvanometer provision for induced emf detection - Load Resistors & Variable Rheostat - Connecting Leads & Safety Terminals ### Accessories Provided-( Test leads , Switches, fuses, and protection devices, Mechanical stand/fixtures for magnet–coil movement, Digital/analogue measurement devices all accessories and practical’s manual (TLM) | 02 No,s |
|  | Advance electrical trainer complete – consist of transformers Test supply (1-Phase-230V /3-Phase -400V) test provision of Single Phase Test (•Open circuit test •short circuit test •Voltage regulation Test ) 3-Phase transformer Test •make connection provision of (Star-Delta, Delta-Delta, Delta-Star), (•vector group Yyo and Yy6, •vector group Ddo and Dd6,• vector group Yd11 and Yd1) With measuring instruments of Digital Meter (Volt, Current, Power, power factor, phase angle),3-phase inductive load and 3-phase Resistive load with all accessories and practical’s operational manual (TLM)including practical diagrams | 02 No,s |
|  | Megger | 05 No,s |
|  | Tong tester/ clamp meter Digital | 05 Nos |
|  | Multi-meter A.C / D.C (Digital) (voltage, Current, OHM, frequency, Uf, Continuity and Diode test) | 05 Nos |
|  | Insulation Test digital | 05 No,s |
|  | Voltage, current and power Digital Panel meter | 05 No,s |
|  | Ampere Digital Panel meter | 05 No,s |
|  | Power Digital Panel meter | 05 No,s |
|  | Electric Hand drill machine with hammering 0-13 mm | 2 Nos |
|  | Pedestal drill machine | 01 Nos |
|  | Jigsaw machine portable | 2 No |
|  | Insulated Scissor 6” | 25 Nos |
|  | Single phase energy meter 220V /10-20A | 05 Nos |
|  | Three phase energy meter 30 A | 05 Nos |
|  | Dust brush / File brush | 05 Nos each |
|  | Magnetic Contactors 2 + 2 220 Volts / 10 A 50Hz | 50 Nos. |
|  | Single Phase Motor 220 Volts 50Hz ½ HP | 03 Nos. |
|  | Three Phase Motor 380 Volts 50Hz 2 HP | 03 Nos. |
|  | Push Button (1-NC&1NO / 2NC&2 NO / 3 NO&3 NC) | 25 Nos. Each |
|  | Change Over Switch -400V/32A | 05 Nos |
|  | Overload Relay 0.5 – 3.0 Amp | 25 Nos. |
|  | Motor Protection Switch Three Phase-400/10A | 05 Nos. |
|  | AC Motor trainer consist of 3-Induction motor (400V/1KW) Copper winding-1-Nos, Magnetic Connector – (Main contact-400V/10A , 2NO,2NC, Coil voltage -220V )-4Nos , Overload Relay-1Nos , Circuit Breaker –(4-Poles- 400V, ELCB ), Push Button- (11NO,NC) 4-Nos,Change Over switch(400V/10A) -1 Nos, indicators – 3Nos , Timer -1 No, connection leads -100Nos , complete with all accessories and practical’s manual (TLM) | 02- Nos |
|  | Level multi dimension | 10 No’s |
|  | Electrician Toolkit – (128-Pcs) | 12 Nos. |
|  | Transformer voltage rating 220V /6V -1A with connection terminal on primary / secondary for training purpose copper winding- with connection Leads – 50Nos | 06Nos |
|  | Transformer voltage rating 220V /12V+12V -5A with connection terminal on primary / secondary for training purpose copper winding- - with connection Leads – 50Nos | 06Nos |
|  | Transformer voltage rating 400V / 24V 1000VA current rating -5A iron steel sheet core, with connection terminal on primary / secondary for training purpose copper winding- with connection Leads – 50Nos | 06Nos |
|  | Auto Transformer three phase rating (2000VA, 0-400V/5A) for training purpose with connection Leads – 20Nos | 05Nos |
|  | Auto transformer single phase rating (1000VA, 0-230V, 5 Amp, 50c/s) copper winding for training purpose - with connection Leads – 20Nos | 05 Nos |
|  | Tachometer (RPM) digital | 03Nos |
|  | Variable Power Supply for AC Voltage/ single phase voltage (1 - 230V) current rating -5A with output terminal connection Leads – 20Nos includes the operation instruction manual | 03Nos |
| 69 | Variable Power Supply for AC Voltage/ 3-Phase voltage (1 - 400V) current rating -5A output terminal with connection Leads – 20Nos includes the operation instruction manual | 03Nos |
| 70 | Variable DC power supply Output Voltage: 0-48-V, Input Voltage: 230V AC, Display: digital Multi O/P 0-30V, 5A/15V, 2A. Short circuit protection, overload protection. Better Load & Line Regulation. Very Low Ripple. Sturdy | 03Nos |
| 71 | # Digital Power Clamp Meterwith specification AC current (A)-400A, AC voltage (V)600V- Active power (W)0.01kW~600kW, Apparent power (VA), 0.01kVA~600kV-A, Reactive power (VAr)0.01kVAr~600kVAr, Power factor 0.3~1, Phase angle (°), 0°~360°, Active energy (Wh)-1kWh~9999kWh, True RMS-( AC Voltage/AC Current), with all accessories | 03Nos |
| 72 | # Phase Sequence 400 V 3-phase power phase sequence - (Digital) | 05Nos |
| 73 | # Coils with iron core | 05Nos |
| 74 | # Galvanometer | 05Nos |
| 75 | # Magnet Bar | 05Nos |
| 76 | # Winding Machine with digital counter | 03 Nos |
| 77 | # Rheostats | 05Nos |
| 78 | # Earth Tester Meter | 02 Nos |
| 79 | # Lug Punching Machine (Manual & Hydraulic) | 02 Nos |
| 80 | # Winding farma | 05Nos |
| 81 | # NCV Tester (Non-Contact Voltage Tester) | 05 Nos |
| 82 | # Earth Resistance Clamp Meter | 02 Nos |
| 83 | # Wheat Stone Bridge | 02 Nos |

# List of Consumables

| SR.NO | NAME | QTY.REQUIRED |
| --- | --- | --- |
| 1 | Solder wire.500-gram 60/40 | 5 real |
| 2 | Soldering paste /Risen | 10 ten |
| 3 | Grinder Disks | 05 No,s |
| 4 | PVC Pipe/Duct. ½ and ¾ Length of 10 feet | 25 each size |
| 5 | PVC clamp. / Saddle | 5 packet |
| 6 | PVC board.3x3 | 200 No,s |
| 7 | Distribution Box 12’’x12” | 10 No,s |
| 8 | Circuit Breaker. 5A, 10A, 20A ,32A | 10 No,s each |
| 9 | Wooden Screw ½, 1, 1.5 and 2 ‘’ | 5 boxes each |
| 10 | Single pole switch. 10-A, Piano | 100 No,s |
| 11 | Lamp holder pin type, Screw Type | 50 each |
| 12 | Lamp, 100 and 200 watts | 25 No,s |
| 13 | Junction Box ½ and ¾ | 10 dozen |
| 14 | PVC Slotted Wiring Duct | 100 Length |
| 15 | Power plug 30A | 25 No,s |
| 16 | Sockets 3 pin- 30A | 50 No,s |
| 17 | PVC wire 1/0.044 | 15 coil |
| 18 | PVC wire 3/0.029 | 15 coil |
| 19 | PVC wire 7/0.029’’ | 10 coil |
| 20 | PVC Cable 4 core 3/0.029’’ | 02 coil |
| 21 | PVC Cable 4 core 1/0.044’’ | 02 coil |
| 22 | Magnetic Contactor (400-V) coil voltages 220V 2+2, 16A and 10A | 50 No,s each |
| 23 | Overload relay 10A and 6A | 10 No,s each |
| 24 | Hacksaw Blade | 30 No,s |
| 25 | Drill bits kit | 15 No,s |
| 26 | Electrical PVC tapes in a different color | 1000 length |
| 27 | Timer with base | 10 No,s each |
| 28 | Indicators Lamp | 100 No,s each |
| 29 | Connector Bar 10A | 5 Box |
| 30 | Battery 9V | 5 Packet |
| 31 | Cell 1.5 V | 5 Packet |
| 32 | Connection Leads | 100 Nos |
| 33 | Photo copy Paper (Ream) | 10Nos |
| 34 | File Cover | 30 Nos |
| 35 | Bana Plug Connectors | 200Nos |
| 36 | Winding wires assorted size | 05 Kg |
| 37 | Transformer iron core | 02 Kg |
| 38 | Transformer -230V | 06 Nos |
| 39 | PVC Insulation Sleave | 06 Doz |
| 40 | PVC connector Bar -20A | 06 Doz |
| 41 | Earth wire -size 10-mm | 01 Coil |
| 42 | Circuit breaker -230/400V-(ELCB) | 12 Nos |
| 43 | Heat Sleaves | 06 Dozs |
| 44 | Lugs (Copper)-assorted sized and types | 20-Dozs |
| 45 | Transformer PVC BOBBINS- assorted sized and types | 06 Dozs |
| 46 | Resistor | 06Nos |

# Members of Qualification Development Committee

The Qualifications Development Committee consisted of the following members:

| Sr. # | Name | Designation | Organization |
| --- | --- | --- | --- |
|  | Syed Salman Nasir Ali Shah | DACUM Expert/ Director (AA) Academics | P-TEVTA |
|  | Ms. Saima Asghar | DACUM Facilitator | LAHORE |
|  | Muhammad Rehan Qureshi | Senior Instructor Electrical | P-TEVTA |
|  | Muhammad.Saeed | Senior Instructor Electrical | P-TEVTA |
|  | Mr.Maqsood | Senior Instructor Electrical | PVTC |
|  | Mr . Sohaib Hassan | Instructor Electrical | PVTC |
|  | Muhammad Naveed Bsahir | Instructor Electrical | P-TEVTA |